SECTION 15181 - HYDRONIC SPECIALTIES

SECTION 23.21.13 - HYDRONIC PIPING SPECIALTIES

GENERAL

SECTION INCLUDES

Air separators

RELATED SECTIONS

Section - Plumbing Piping Specialties

Section - Hydronic Piping.

REFERENCES

ASME (BPV VIII, 1) - Boiler and Pressure Vessel Code, Section VIII, Division 1 - Rules for Construction of Pressure Vessels; The American Society of Mechanical Engineers; 2006.

SUBMITTALS

See Section 01300 - Administrative Requirements, for submittal procedures.

Product Data: Provide product data for manufactured products and assemblies required for this project. Include component sizes, rough-in requirements, service sizes, and finishes. Include  product description, model and dimensions.

Certificates: Inspection certificates for pressure vessels from authority having jurisdiction.

Manufacturer's Installation Instructions: Indicate hanging and support methods, joining procedures.

Maintenance Data: Include installation instructions, assembly views, and replacement parts list.

QUALITY ASSURANCE

Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum five years of documented experience.

DELIVERY, STORAGE, AND HANDLING

Accept equipment on site in shipping containers with labeling in place. Inspect for damage.

Provide temporary end caps and closures on piping and fittings. Maintain in place until installation.

Protect piping components from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

MAINTENANCE SERVICE

Contractor to furnish service and maintenance for one year from date of substantial completion.

PRODUCTS

AIR SEPARATORS.

Manufacturers:

Grundfos; ___ (strainer) (size and capacity as called for on plans)

Air removal device shall be constructed of steel. It shall be designed, fabricated and stamped per ASME Section VIII Division 1 with a maximum working pressure of 150 psi at 270°F. Manufacturer shall be holder of ASME U stamp. Manufacturer to have optional 250 psi and 125 psi ASME units available. Units 3 inch and larger shall be provided with flanged system connections as standard. 2 inch and 2½ inch models to be provided with NPT connections. These connections shall be inline with the mechanical room piping. The unit shall be painted with one coat of red oxide primer.

The unit shall have a top NPT connection to allow for the tie in of automatic air vent, make up water, and compression tank (air control system). This fitting shall be at the upper most point on the chamber. There shall be a bottom connection for blowdown cleaning.

(OPTIONAL) The unit shall be provided with a removable stainless steel strainer with 3/16” perforations and a free area of not less than five times the cross sectional area of the connecting pipe. The unit shall come with an inline connection that will allow for strainer removal. This additional fitting shall allow the installing contractor the option of installing the unit with inlet and outlet on the same side of the unit or on opposite sides.

EXECUTION

INSTALLATION

Install specialties in accordance with manufacturer's instructions.

Where large air quantities can accumulate, provide enlarged air collection standpipes.

Provide manual air vents at system high points and as indicated.

For automatic air vents in ceiling spaces or other concealed locations, provide vent tubing to nearest drain.

Air separator and to be installed on the suction side of the system pumps.

Provide valved drain and hose connection on strainer blow down connection.

Provide relief valves on pressure tanks, low pressure side of reducing valves, heat exchangers, and expansion tanks.

END OF SECTION 15181 /  23.21.13