SECTION 15181 - HYDRONIC SPECIALTIES

SECTION 23.21.13 - HYDRONIC PIPING SPECIALTIES

GENERAL

SECTION INCLUDES

Expansion tanks

RELATED SECTIONS

Section - Plumbing Piping Specialties

Section - Hydronic Piping.

REFERENCES

ASME (BPV VIII, 1) - Boiler and Pressure Vessel Code, Section VIII, Division 1 - Rules for Construction of Pressure Vessels; The American Society of Mechanical Engineers; 2006.

SUBMITTALS

See Section 01300 - Administrative Requirements, for submittal procedures.

Product Data: Provide product data for manufactured products and assemblies required for this project. Include component sizes, rough-in requirements, service sizes, and finishes. Include  product description, model and dimensions.

Certificates: Inspection certificates for pressure vessels from authority having jurisdiction.

Manufacturer's Installation Instructions: Indicate hanging and support methods, joining procedures.

Maintenance Data: Include installation instructions, assembly views, and replacement parts list.

QUALITY ASSURANCE

Manufacturer Qualifications: Company specializing in manufacturing the type of products specified in this section, with minimum five years of documented experience.

DELIVERY, STORAGE, AND HANDLING

Accept equipment on site in shipping containers with labeling in place. Inspect for damage.

Provide temporary end caps and closures on piping and fittings. Maintain in place until installation.

Protect piping components from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

MAINTENANCE SERVICE

Contractor to furnish service and maintenance for one year from date of substantial completion.

PRODUCTS

ASME Full Bladder TYPE EXPANSION TANKS

Manufacturers:

Grundfos

Construction: Welded steel, designed, tested and stamped in accordance with ASME (BPV code sec VIII, div 1); supplied with National Board Form U-1, rated for working pressure of 150 psi , with flexible heavy duty butyl rubber bladder. Bladder shall be able to accept the full volume of the expansion tank and shall be removable and replaceable. Bladder shall be NSF 61 rated for low temperature potable water service and shall be manufactured with FDA approved materials.

Accessories: Pressure gage (field installed in adjacent piping by others) and air-charging fitting ; precharge to ____ psi.

Automatic Cold Water Fill Assembly (field installed by others): Pressure reducing valve, reduced pressure double check back flow preventer, test cocks, strainer, vacuum breaker, and valved by-pass.

Size:

HW Tank Capacity: ___________., _____________ acceptance volume.

CW Tank Capacity: ___________., _____________ acceptance volume.

Hot Water Heating System:

Select expansion tank pressure relief valve at _____ psi maximum.

Set pressure reducing valve at ____ psi.

Chilled Water System:

Select expansion tank pressure relief valve at _____ psi maximum.

Set pressure reducing valve at _____ psi.

EXECUTION

INSTALLATION

Install specialties in accordance with manufacturer's instructions.

Where large air quantities can accumulate, provide enlarged air collection standpipes.

Provide manual air vents at system high points and as indicated.

For automatic air vents in ceiling spaces or other concealed locations, provide vent tubing to nearest drain.

Expansion tank to be installed on the suction side of the system pumps. Expansion tank to be tied into system piping in close proximity to air separator and system fill line.

Provide valved drain and hose connection on strainer blow down connection.

Provide relief valves on pressure tanks, low pressure side of reducing valves, heat exchangers, and expansion tanks.

END OF SECTION 15181 /  23.21.13