# TYPE GRD & GSD

The contractor shall furnish and install a PACO (Simplex, duplex) automatic (condensate, boiler feed) unit, each pump shall deliver _____ GPM at _____ PSI at the pump.  Pumps shall be mounted vertically and flanged to the receiver.  Pumps shall be bronze fitted end suction centrifugal pumps with 210oF mechanical seals close coupled to _____ HP (single, three) phase (115, 208, 230, 460) volt, 60 Hertz, (1750, 3500) RPM, (open drip-proof, totally enclosed) electric motors.  A vent line shall be furnished from each pump seal chamber to the receiver.

# TYPE GRD

Receiver shall be heavy wall _____ gallon cast iron with 2” vent, ¾” drain and (2”, 3”) inlet.

## TYPE GSD

Receiver shall be _____ gallon 3/16” black steel with 2” vent, ¾” drain and (2”, 3”) inlet.

Simplex unit shall include Nema I Square D class 9037 float switch assembly.  Duplex unit shall include Nema I Square D class 9038 mechanical alternator (with, without) auxiliary standby float switch (or) two Square D class 9037 float switches with electric alternator in panel.

# TYPE BRD & BSD

Boiler feed simplex or duplex units will be furnished with Square D class 9038 float switch and ½” solenoid makeup valve mounted on vent pipe line with air gap on CI tanks and on 1 ½” opening on top of 3/16” black steel tanks with air gap.

# Optional Equipment

- ½” water gauge glass with stopcock.

- Wye type inlet strainer (2”, 3”).

- 2 ½” dial thermometer.

- Type GSD receivers can be furnished in stainless steel or galvanized steel construction.

- ¾” solenoid on larger units.

- Magnetic motor starters with HOA switch shall be furnished for each pump motor (mounted and wired on receiver, for remote mounting) Nema I enclosures.

- Duplex control panel with magnetic starters, HOA switches, (with, without) circuit breakers 115 volt control circuit transformer, 3rd leg overload protection, terminal strip, Nema I enclosure shall be furnished (mounted on receiver & wired, for remote wall mounting) Nema I enclosure (with, without) electric alternator.