# Typical Specifications

SCOPE: Furnish and install________ submersible non-clog sewage pump (s). Each pump shall be capable of delivering the following performance points,: ____________ U.S. GPM at ____________ TDH; ____________U.S. GPM at __________ TDH; ___________U.S. GPM at _____________TDH, with a shut off head of __________TDH (minimum). The pump motor speed shall be 1750 RPM, ____________HP (maximum), __________Phase, 60 Hertz, ____________Volts. The pump (s) shall be manufactured in North America by a company regularly engaged in the manufacture and assembly of similar units for a minimum of five (5) years. The pump (s) shall be Sulzer Pumps Houston Inc.  model_____________________.

PUMP DESIGN: Each pump shall be capable of handling raw,

unscreened domestic sewage consisting of water, fibrous materials, and _____ inch diameter spherical solids. The pump (s) shall be capable of handling liquids with temperatures to 104 degrees F continuous, 160 degrees F intermittent, and shall be capable of running dry for extended periods.

PUMP CONSTRUCTION: The volute, seal plates, impeller and motor housing shall be constructed of high quality ASTM A-48 class 30 cast iron. The pump (s) shall be painted with a water based air dry enamel of 2.0 mil minimum thickness. All exposed hardware shall be 300 series stainless steel. The pump construction shall contain no points of critical

clearance nor require periodic adjustment or replacement to maintain operating efficiency. Discharge connection shall be a standard________ inch NPT in the vertical position. All gaskets shall be of the compression square ring type eliminating critical slip fits and the possibility of damage during service associated with sliding o-ring sealing arrangements.

The impeller shall be of the non-clog design with pump out vanes on the back side. The impeller shall be dynamically balanced to ISO G6.3 specifications. The unit shall utilize a single mechanical shaft seal which will operate in an oil atmosphere. The materials of construction shall be carbon

for the rotating face and ceramic for the stationary face, lapped and polished to a tolerance of one light band, 300 series stainless steel hardware, and all elastomer parts to be of Buna-N. The seal shall be commercially available and not a proprietary design of the manufacturer.  The pump shall be designed to be non-overloading throughout the entire pump curve. The rotor and stator assembly shall be of the standard frame design and secured to the pump seal plate by four

threaded fasteners allowing for easy serviceability. Motor designs incorporating shrink or press fit assembly between the stator and motor housing shall not be acceptable. The motor shall be constructed with the windings operating in a sealed environment containing clean dielectric oil, making it capable of operating in a totally, partially or non-submerged

condition for extended periods of time without damage due

to the heat being generated..

The motor windings shall be of Class B insulation. The motor shall meet the standard NEMA design L for single phase and NEMA design B for three phase. The motor shaft shall be of 416 stainless steel. The lower bearing shall be of the single ball type to accept radial and thrust loads, and the upper bearing of the single ball design, for radial loads.  Bearings shall operate in an oil bath atmosphere for superior life.  Permanently lubricated bearings are not acceptable.  Thermal sensor shall be used on three phase units to monitor stator temperatures. The stator shall be equipped with a thermal switch embedded in the end coil of the stator winding. This shall be used in

conjunction with external motor overload protection and wired to the control panel. Single phase shall have an overload

switch on the motor windings and do not require any external protection.  The pump shall be equipped with _______ft. of type SOW or SJTOW power cable and connected to the motor via quick disconnect pin terminals.  Threaded cord grip type cord entries are not acceptable. Pin receptacles shall be crimped and molded to the power cord in a PVC plug. The plug

shall be secured with a stainless steel compression plate to prevent water from entering the housing and to provide strain relief at the point of cable entry. A stainless steel clamp shall compress the PVC molding against the cable jacket to prevent water from entering the jacket. A polybutylene terephthalate terminal block with brass pin inserts shall connect the power cord leads with the motor leads. The ground pin shall be longer than the other pins such that the ground connection is the first connection made and the last connection broken when the plug

is inserted and removed, respectively. A Buna-N o-ring shall provide isolation sealing between the terminal block and the motor housing when the cord plug is removed.

PUMP TEST: The pump manufacturer shall perform the following inspections and tests in accordance with Hydraulic Institute type B standards before shipment from the factory:

1. A check of the motor voltage and frequency shall be made as shown on the name plate.

2. A motor and cable insulation test for moisture content or

insulation defects shall be made per UL criteria.

3. The pump shall be completely submerged and run to determine that the unit meets three pre-determined hydraulic performance points.

4. A written report shall be available showing the aforementioned tests have been performed in accordance with the specifications.

START-UP: The pump(s) shall be tested at start-up by a qualified representative of the manufacturer. A start-up report as provided by the manufacturer shall be completed before final acceptance of the pump(s).