The contractor shall furnish and install, as shown in the drawings and as described in these specifications, PACO Type VLS Vertical In-Line bronze fitted, single stage, centrifugal pump(s), as manufactured by PACO Pumps.

Each pump shall be capable of delivering _____ gallons per minute against a total head of _____ feet.  Pump(s) shall meet or exceed the efficiency shown in the pump schedule.

To insure stable operation, the pump curve shall be constantly rising from run-out to shut off.  To insure cavitation-free operation, each pump’s NPSH requirement must be low enough to permit stable, continuous operation at 120% or greater of best efficiency point.  Each pump shall be capable of continuous operation without producing noise in excess of Hydraulic Institute and OSHA guidelines.

Pump(s) shall (each) be rigid coupled to a _____ HP, _____ RPM, _____ phase, _____ Hertz, _____ volt ball bearing drip-proof (special enclosure, specify: _____) Nema (standard, high efficiency) electric motor.  Motor shall be of such size that it will operate continuously without exceeding its HP rating, exclusive of service factor, at the design capacity and head. Motor shall be of a C-face design with a lockable split collar on motor side to facilitate precise positioning of rotating assembly with reference to Hydraulic geometry. P-base design motors shall be acceptable.

Pump shall be connected to the drive motor by a rigid, ductile iron, radially split coupling capable of withstanding all torsional, radial and axial loads. The coupling design shall facilitate alignment of motor and pump shaft. The coupling design shall also permit replacement of mechanical seal without requiring removal of the drive motor. Coupling and exposed rotating components of the pump and motor shall be protected by OSHA approved guard.

Pump casing shall be gray iron and shall be constructed with back pull-out capability.  Models 3” and larger shall have balanced double volute design to reduce radial thrust and to prolong seal and bearing life.  Pump casing shall incorporate a suction baffle to reduce pre-rotation and improve efficiency.  Suction and Discharge connections shall be the same size, flanged (125, 250) PSI rating, 180 degrees opposite on centerline for pipeline mounting.  Casing shall have bronze replaceable wear ring.  Impeller shall be cast bronze, enclosed, statistically, dynamically and hydraulically balanced, and shall be factory trimmed to match the delivery conditions indicated above.  Pump shaft shall be stainless steel. Pumps shall have mechanical seal suitable for the temperatures and pressures indicated, and shall be properly vented to the pump suction connection.

All normally required spare and replacement parts shall be available in kit form and shall be field selectable from pump nameplate data.  It shall not be necessary to reference any drawing when selecting spare or replacement parts.

Optional Supports: Pump shall be mounted on a heavy duty cast iron support stand or on steel flange supports for floor mounting (Note: Specify one if applicable). Factory recommendation for mounting: 25HP and below unit can be suspended on the ceiling. 30HP and above unit shall have cast iron support.